## NSF
SEPTIC TANK |  |  |  |  | "NSF"Scenario Applied To AZ Home |  | 7 Hydraulic loading to field (design requirement): |  | 0.6 | GPD/sqft
INPUT NUMBERS | [6 empty] | CALCULATED NUMBERS | [5 empty] | COMPARISON | COMPARISON
|  |  |  | 2 Wastewater | 3 Graywater |  |  |  | 5 Typical | 6 Effluent | 7 Organic | 8 Potential | 9 Typical Septic Tank | 10 AZ Effluent Strength
#people | Number of | 1 Flow per person | Wastewater | Tot. Influent | Estimated | 4 Graywater | Tank Influent | Tank Influent | Septic Tank | Strength | Loading to Field | Conversion | Effluent Strength | R-18-9-E302 B
per bedroom | Bedrooms | GPD | Components | Strength | Strength | Flow % to reuse | Flow GPD | Strength | Efficiency % | to Field | lbs/sqft/day | in Field
2 | 2 | 75 | TSS, mg/l | 225 | 120 | 72% | 84 | 495 | 70% | 148.5 |  | 1.485 | 101 | 75
|  |  | BOD, mg/l | 200 | 155 |  |  | 315.7143 | 40% | 189.4286 | 0.00094631 | 1.8943 | 147 | 150
|  |  | TKN, mg/l | 50 | 5 |  |  | 165.7143 | 10% | 149.1429 |  | 110.5514 | 68 | 53
|  |  | NO3-N, mg/l | 0 | 0 |  |  | 0 | 0% | 0 |  | 19.6486 | 0 | NA
|  |  | FOG, mg/l | 87.5 | 9 |  |  | 289.3571 | 79% | 60.765 |  | 0.60765 | 36 | NA
|  |  | Alkalinity, mg/l | 175 | 158 |  |  | 218.7143 | 0% | 218.7143 |  | - | - | NA
1 Flow based on 2-3 bedroom home in AZ
2 Influent NSF Standard 40 median except FOG which is taken from EPA manual, table 3-7 range of 70 to 105 mg/l, median 87.5 mg/l.
Hydraulic loading rate: |  |  | 84 | GPD | 3 Graywater Estimated TSS, BOD from NSF Standard 245 Median. TKN, FOG assumed.
Alkalinity mean of 158 mg/l from Tier Two and Three Greywater Subsurface Irrigation Systems/Guidance, Washington State, pg 14.
Tank Volume | 1000 | Gal |  |  | 4 Graywater is reused , i.e. does not enter tank
Retention Time | 285.7143 | hrs |  |  | Flow % from WERF Long Term Effects Of Landscape Irrigation Using Household Graywater-Literature Review And Synthesis, 2006.
5 TSS, BOD from EPA as decribed. Nitrogen assumed. FOG from Seabloom, Bounds, Louden. Alkalinity no data.
6 If BOD, TSS & FOG are higher than typical numbers, the drain field needs to be larger
(could still cause severe clogging & biomat formation otherwise)
7 Typical rock & pipe trench and hydraulic loading information provided by Peter Livingston, Bosque Engineering, Tucson, AZ.
8 Assumes enough oxygen is available for nitrification in aerobic zone of field; alkalinity comes from effluent only
Denitrification assumes 50% of effluent BOD is available in anaerobic zone of field
Assumes complete removal (99%) in field of TSS, BOD, & FOG
9 Average numbers from EPA Onsite Wastewater Treatment Manual
10 Numbers from Title 18 Chapter 9 Arizona Administrative Code

## AZ
SEPTIC TANK |  |  |  |  | AZ Scenario |  | 7 Hydraulic loading to field (design requirement): |  | 0.6 | GPD/sqft
INPUT NUMBERS | [6 empty] | CALCULATED NUMBERS | [5 empty] | COMPARISON | COMPARISON
|  |  |  | 2 Wastewater | 3 Graywater |  |  |  | 5 Typical | 6 Effluent | 7 Organic | 8 Potential | 9 Typical Septic Tank | 10 AZ Effluent Strength
#people | Number of | 1 Flow per person | Wastewater | Tot. Influent | Estimated | 4 Graywater | Tank Influent | Tank Influent | Septic Tank | Strength | Loading to Field | Conversion | Effluent Strength | R-18-9-E302 B
per bedroom | Bedrooms | GPD | Components | Strength | Strength | Flow % to reuse | Flow GPD | Strength | Efficiency % | to Field | lbs/sqft/day | in Field
2 | 2 | 75 | TSS, mg/l | 430 | 35.09 | 86% | 42 | 2855.8757 | 83% | 485.4989 |  | Field Overload! | 101 | 75
|  |  | BOD, mg/l | 380 | 64.85 |  |  | 2315.9214 | 61% | 903.2094 | 0.0045121 | Field Overload! | 147 | 150
|  |  | TKN, mg/l | 53 | 5 |  |  | 347.8571 | 0% | 347.8571 |  | 270.7715 | 68 | 53
|  |  | NO3-N, mg/l | 0 | 0 |  |  | 0 | 0% | 0 |  | 2 | 0 | NA
|  |  | FOG, mg/l | 75 | 8 |  |  | 486.5714 | 79% | 102.18 |  | 1.0218 | 36 | NA
|  |  | Alkalinity, mg/l | 175 | 158 |  |  | 279.4286 | 0% | 279.4286 |  | - | - | NA
1 Flow based on 2-3 bedroom home in AZ
2 Influent values taken from ADEQ page 5, item 42, “Typical Sewage”. Alkalinity NSF Standard 40.
Hydraulic loading rate: |  |  | 42 | GPD | 3 TSS and BOD taken from Casanova, Gerba and Karpiscak 2001, Casa Del Agua Study. Nitrogen and FOG assumed.
Alkalinity mean of 158 mg/l from Tier Two and Three Greywater Subsurface Irrigation Systems/Guidance, Washington State, pg 14.
Tank Volume | 1000 | Gal |  |  | 4 Graywater is reused , i.e. does not enter tank.
Retention Time | 571.4286 | hrs |  |  | Flow % from Charles P. Gerba Powerpoint Presentation. Pg 12-13. Sources Of Graywater In Pima County.
5 TSS, BOD & Nitrogen calculated w/ ADEQ influent & effluent strengths. FOG from Seabloom, Bounds, Louden. Alkalinity no data
6 If BOD, TSS & FOG are higher than typical numbers, the drain field needs to be larger
(could still cause severe clogging & biomat formation otherwise)
7 Typical rock & pipe trench and hydraulic loading information provided by Peter Livingston, Bosque Engineering, Tucson, AZ.
8 Assumes enough oxygen is available for nitrification in aerobic zone of field; alkalinity comes from effluent only
Denitrification assumes 50% of effluent BOD is available in anaerobic zone of field
Assumes complete removal (99%) in field of TSS, BOD, & FOG
9 Average numbers from EPA Onsite Wastewater Treatment Manual
10 Numbers from Title 18 Chapter 9 Arizona Administrative Code

## AZ Broad
SEPTIC TANK |  |  |  |  | AZ/Broad Scenario |  | 7 Hydraulic loading to field (design requirement): |  | 0.6 | GPD/sqft
INPUT NUMBERS | [6 empty] | CALCULATED NUMBERS | [5 empty] | COMPARISON | COMPARISON
|  |  |  | 2 Wastewater | 3 Graywater |  |  |  | 5 Typical | 6 Effluent | 7 Organic | 8 Potential | 9 Typical Septic Tank | 10 AZ Effluent Strength
#people | * Number of | 1 Flow per person | Wastewater | Tot. Influent | Estimated | 4 Graywater | Tank Influent | Tank Influent | Septic Tank | Strength | Loading to Field | Conversion | Effluent Strength | R-18-9-E302 B
per bedroom | Bedrooms | GPD | Components | Strength | Strength | Flow % to reuse | Flow GPD | Strength | Efficiency % | to Field | lbs/sqft/day | in Field
2.58 | 1 | 66.9 | TSS, mg/l | 225 | 35.09 | 72% | 48.3286 | 713.34 | 70% | 214.002 |  | Field Overload! | 101 | 75
|  |  | BOD, mg/l | 200 | 64.85 |  |  | 547.5286 | 40% | 328.5171 | 0.0016411 | Field Overload! | 147 | 150
|  |  | TKN, mg/l | 50 | 5 |  |  | 165.7143 | 10% | 149.1429 |  | 104.7074 | 68 | 53
|  |  | NO3-N, mg/l | 0 | 0 |  |  | 0 | 0% | 0 |  | 11.5838 | 0 | NA
|  |  | FOG, mg/l | 87.5 | 8 |  |  | 291.9286 | 79% | 61.305 |  | 0.61305 | 36 | NA
|  |  | Alkalinity, mg/l | 175 | 158 |  |  | 218.7143 | 0% | 218.7143 |  | - | - | NA
* I input 1 to use census data for calculation. Not literally a 1 bedroom home.
1 2010 Census persons per household Tucson, AZ and EPA Table 3-2.
2 Influent NSF Standard 40 Median except FOG which is taken from EPA manual, table 3-7 range of 70 to 105 mg/l, median 87.5 mg/l.
Hydraulic loading rate: |  |  | 48.3286 | GPD | 3 TSS and BOD taken from Casanova, Gerba and Karpiscak 2001, Casa Del Agua Study. Nitrogen and FOG assumed.
Alkalinity mean of 158 mg/l from Tier Two and Three Greywater Subsurface Irrigation Systems/Guidance, Washington State, pg 14.
Tank Volume | 1000 | Gal |  |  | 4 Graywater is reused , i.e. does not enter tank
Retention Time | 496.6008 | hrs |  |  | WERF Long Term Effects Of Landscape Irrigation Using Household Graywater-Literature Review And Synthesis, 2006.
5 TSS, BOD from EPA as decribed. Nitrogen assumed. FOG from Seabloom, Bounds, Louden. Alkalinity no data.
6 If BOD, TSS & FOG are higher than typical numbers, the drain field needs to be larger
(could still cause severe clogging & biomat formation otherwise)
7 Typical rock & pipe trench and hydraulic loading information provided by Peter Livingston, Bosque Engineering, Tucson, AZ.
8 Assumes enough oxygen is available for nitrification in aerobic zone of field; alkalinity comes from effluent only
Denitrification assumes 50% of effluent BOD is available in anaerobic zone of field
Assumes complete removal (99%) in field of TSS, BOD, & FOG
9 Average numbers from EPA Onsite Wastewater Treatment Manual
10 Numbers from Title 18 Chapter 9 Arizona Administrative Code

## Play
SEPTIC TANK |  |  |  |  | AZ/Broad/Play |  | 7 Hydraulic loading to field (design requirement): |  | 0.6 | GPD/sqft
INPUT NUMBERS | [6 empty] | CALCULATED NUMBERS | [5 empty] | COMPARISON | COMPARISON
|  |  |  | 2 Wastewater | 3 Graywater |  |  |  | 5 Typical | 6 Effluent | 7 Organic | 8 Potential | 9 Typical Septic Tank | 10 AZ Effluent Strength
#people | * Number of | 1 Flow per person | Wastewater | Tot. Influent | Estimated | 4 Graywater | Tank Influent | Tank Influent | Septic Tank | Strength | Loading to Field | Conversion | Effluent Strength | R-18-9-E302 B
per bedroom | Bedrooms | GPD | Components | Strength | Strength | Flow % to reuse | Flow GPD | Strength | Efficiency % | to Field | lbs/sqft/day | in Field
2.58 | 1 | 66.9 | TSS, mg/l | 225 | 35.09 | 72% | 48.3286 | 713.34 | 70% | 214.002 |  | Field Overload! | 101 | 75
|  |  | BOD, mg/l | 200 | 64.85 |  |  | 547.5286 | 40% | 328.5171 | 0.0016411 | Field Overload! | 147 | 150
|  |  | TKN, mg/l | 50 | 5 |  |  | 165.7143 | 10% | 149.1429 |  | 104.7074 | 68 | 53
|  |  | NO3-N, mg/l | 0 | 0 |  |  | 0 | 0% | 0 |  | 11.5838 | 0 | NA
|  |  | FOG, mg/l | 87.5 | 8 |  |  | 291.9286 | 79% | 61.305 |  | 0.61305 | 36 | NA
|  |  | Alkalinity, mg/l | 175 | 158 |  |  | 218.7143 | 0% | 218.7143 |  | - | - | NA
* I input 1 to use census data for calculation. Not literally a 1 bedroom home.
1 2010 Census persons per household Tucson, AZ and EPA Table 3-2.
2 Influent NSF Standard 40 Median except FOG which is taken from EPA manual, table 3-7 range of 70 to 105 mg/l, median 87.5 mg/l.
Hydraulic loading rate: |  |  | 48.3286 | GPD | 3 TSS and BOD taken from Casanova, Gerba and Karpiscak 2001, Casa Del Agua Study. Nitrogen and FOG assumed.
Alkalinity mean of 158 mg/l from Tier Two and Three Greywater Subsurface Irrigation Systems/Guidance, Washington State, pg 14.
Tank Volume | 1000 | Gal |  |  | 4 Graywater is reused , i.e. does not enter tank
Retention Time | 496.6008 | hrs |  |  | WERF Long Term Effects Of Landscape Irrigation Using Household Graywater-Literature Review And Synthesis, 2006.
5 TSS, BOD from EPA as decribed. Nitrogen assumed. FOG from Seabloom, Bounds, Louden. Alkalinity no data.
6 If BOD, TSS & FOG are higher than typical numbers, the drain field needs to be larger
(could still cause severe clogging & biomat formation otherwise)
7 Typical rock & pipe trench and hydraulic loading information provided by Peter Livingston, Bosque Engineering, Tucson, AZ.
8 Assumes enough oxygen is available for nitrification in aerobic zone of field; alkalinity comes from effluent only
Denitrification assumes 50% of effluent BOD is available in anaerobic zone of field
Assumes complete removal (99%) in field of TSS, BOD, & FOG
9 Average numbers from EPA Onsite Wastewater Treatment Manual
10 Numbers from Title 18 Chapter 9 Arizona Administrative Code